## Objects
Object Name | Data Type | Units | Object Number | Property Identifier | Description | Valid Input Values | Default Value | Writeable: N, Y, R, U
Device Object (Object_Type = 8)
Device | BACnetObjectIdentifier |  | Serial# | Object_Identifier (75) | Network-wide unique identifier. Defaults to serial number. This is also called the Device Identifier | 0 to 4194303 | Device, Serial# | Y,U
Device | String |  | Serial# | Object_Name (77) | Network-wide unique name. Defaults to model and serial number | none | CalModel, Serial# | N
Device | BACnetObjectType |  | Serial# | Object_Type (79) | 8 = Device object type | none | 8 | N
Device | BACnetDeviceStatus |  | Serial# | System_Status (112) | 0 = operational | none | 0 | N
Device | String |  | Serial# | Vendor_Name (121) | Manufacturer | none | Continental Control Systems, LLC | N
Device | UInt16 |  | Serial# | Vendor_Identifier (120) | Unique ID assigned by ASHRAE | none | 500 | N
Device | String |  | Serial# | Model_Name (70) | The product model number | none |  | N
Device | String |  | Serial# | Firmware_Revision (44) | The product firmware version | none | 1.2 | N
Device | String |  | Serial# | Application_Software_Version (12) | The product application version (same as firmware version) | none | 1.2 | N
Device | String |  | Serial# | Location (58) | User configurable location string | 30 characters | Unspecified | Y,U
Device | String |  | Serial# | Description (28) | User configurable description string | 30 characters | AC Power and Energy Meter | Y,U
Device | Unsigned |  | Serial# | Protocol_Version (98) | BACnet protocol version | none | 1 | N
Device | Unsigned |  | Serial# | Protocol_Revision (139) | BACnet protocol revision | none | 1 | N
Device | BACnetServicesSupported |  | Serial# | Protocol_Services_Supported (97) | List of all the BACnet services the device supports | none | AtomicWriteFile, ReadProperty, ReadPropertyMultiple, WriteProperty, WritePropertyMultiple, ReinitializeDevice, WhoIs, WhoHas | N
Device | BACnetObjectTypesSupported |  | Serial# | Protocol_Object_Types_Supported (96) | List of all the BACnet objects supported | none | Analog Input, Analog Value, Binary Value, Device, Multi-state Value, File Object | N
Device | BACnetARRAY[N] of ObjectId |  | Serial# | Object_List (76) | List of all the objects | none |  | N
Device | Unsigned |  | Serial# | Max_APDU_Length_Accepted (62) | Maximum application data length | none | 480 | N
Device | BACnetSegmentation |  | Serial# | Segmentation_Supported (107) | 3 = "no segmentation" | none | 3 | N
Device | Unsigned | milliseconds | Serial# | APDU_Timeout (11) | Application request timeout in milliseconds. The WattNode does not initiate requests. | none | 0 | N
Device | Unsigned |  | Serial# | Number_Of_APDU_Retries (73) | Application request retries | none | 3 | N
Device | List of BACnetAddressBinding |  | Serial# | Device_Address_Binding (30) | The WattNode does not initiate service requests, so does not maintain a binding list. It will always report an empty list. | none |  | N
Device | UInt8 |  | Serial# | Max_Master (64) | Highest possible address for master nodes | none | 127 | N
Device | Unsigned |  | Serial# | Max_Info_Frames (63) | Max number of information frames the node may send before passing the token | none | 1 | N
Device | Unsigned |  | Serial# | Database_Revision (155) | Increments when the device object ID is changed | none | 1 | N
Device | BACnetRestartReason |  | Serial# | Last_Restart_Reason(196) | This is the reason for the most recent device restart | none | 0 | N
Analog Input Objects (Object_Type = 0)
EnergySumNR | Float | Kilowatt Hours | 0 | Present_Value (85) | Energy, total net (kWh) non-resettable | none |  | N
EnergySumNRInt | Int32 | 0.1 Kilowatt Hours | 0 | Integer_Value (1000) | Energy, total net (kWh) non-resettable | none |  | N
EnergyPosSumNR | Float | Kilowatt Hours | 1 | Present_Value (85) | Energy, total positive (kWh) non-resettable | none |  | N
EnergyPosSumNRInt | Int32 | 0.1 Kilowatt Hours | 1 | Integer_Value (1000) | Energy, total positive (kWh) non-resettable | none |  | N
EnergyNegSumNR | Float | Kilowatt Hours | 2 | Present_Value (85) | Energy, total negative (kWh) non-resettable | none |  | N
EnergyNegSumNRInt | Int32 | 0.1 Kilowatt Hours | 2 | Integer_Value (1000) | Energy, total negative (kWh) non-resettable | none |  | N
PowerSum | Float | Watts | 3 | Present_Value (85) | Power, total | none |  | N
PowerA | Float | Watts | 4 | Present_Value (85) | Power, phase A (watts) | none |  | N
PowerB | Float | Watts | 5 | Present_Value (85) | Power, phase B (watts) | none |  | N
PowerC | Float | Watts | 6 | Present_Value (85) | Power, phase C (watts) | none |  | N
PowerReacSum | Float | Volt Amperes Reactive | 7 | Present_Value (85) | Reactive power, total | none |  | N
PowerReacA | Float | Volt Amperes Reactive | 8 | Present_Value (85) | Reactive power, phase A | none |  | N
PowerReacB | Float | Volt Amperes Reactive | 9 | Present_Value (85) | Reactive power, phase B | none |  | N
PowerReacC | Float | Volt Amperes Reactive | 10 | Present_Value (85) | Reactive power, phase C | none |  | N
PowerAppSum | Float | Volt Amperes | 11 | Present_Value (85) | Apparent power, total | none |  | N
PowerAppA | Float | Volt Amperes | 12 | Present_Value (85) | Apparent power, phase A | none |  | N
PowerAppB | Float | Volt Amperes | 13 | Present_Value (85) | Apparent power, phase B | none |  | N
PowerAppC | Float | Volt Amperes | 14 | Present_Value (85) | Apparent power, phase C | none |  | N
VoltAvgLN | Float | Volts | 15 | Present_Value (85) | Voltage, average, line-to-neutral | none |  | N
VoltA | Float | Volts | 16 | Present_Value (85) | Voltage, phase A, line-to-neutral | none |  | N
VoltB | Float | Volts | 17 | Present_Value (85) | Voltage, phase B, line-to-neutral | none |  | N
VoltC | Float | Volts | 18 | Present_Value (85) | Voltage, phase C, line-to-neutral | none |  | N
VoltAvgLL | Float | Volts | 19 | Present_Value (85) | Voltage, average, line-to-line | none |  | N
VoltAB | Float | Volts | 20 | Present_Value (85) | Voltage, phase A-B, line-to-line | none |  | N
VoltBC | Float | Volts | 21 | Present_Value (85) | Voltage, phase B-C, line-to-line | none |  | N
VoltAC | Float | Volts | 22 | Present_Value (85) | Voltage, phase A-C, line-to-line | none |  | N
Freq | Float | Hertz | 23 | Present_Value (85) | Line frequency (Hz) | none |  | N
CurrentA | Float | Amperes | 24 | Present_Value (85) | Current, phase A | none |  | N
CurrentB | Float | Amperes | 25 | Present_Value (85) | Current, phase B | none |  | N
CurrentC | Float | Amperes | 26 | Present_Value (85) | Current, phase C | none |  | N
PowerFactorAvg | Float | No Units | 27 | Present_Value (85) | Power factor, average | none |  | N
PowerFactorA | Float | No Units | 28 | Present_Value (85) | Power factor, phase A | none |  | N
PowerFactorB | Float | No Units | 29 | Present_Value (85) | Power factor, phase B | none |  | N
PowerFactorC | Float | No Units | 30 | Present_Value (85) | Power factor, phase C | none |  | N
Demand | Float | Watts | 31 | Present_Value (85) | Demand, power sum | none |  | R, U
DemandApp | Float | Watts | 32 | Present_Value (85) | Demand, apparent power | none |  | R, U
DemandA | Float | Watts | 33 | Present_Value (85) | Demand, power, phase A | none |  | R, U
DemandB | Float | Watts | 34 | Present_Value (85) | Demand, power, phase B | none |  | R, U
DemandC | Float | Watts | 35 | Present_Value (85) | Demand, power, phase C | none |  | R, U
DemandMin | Float | Watts | 36 | Present_Value (85) | Demand, minimum | none |  | R, U
DemandMax | Float | Watts | 37 | Present_Value (85) | Demand, maximum | none |  | R, U
EnergySum | Float | Kilowatt Hours | 38 | Present_Value (85) | Energy, total net (kWh) | ±100GWh |  | Y, R, U
EnergySumInt | Int32 | 0.1 Kilowatt Hours | 38 | Integer_Value (1000) | Energy, total net (kWh) | ±100GWh |  | Y, R, U
EnergyPosSum | Float | Kilowatt Hours | 39 | Present_Value (85) | Energy, total positive (kWh) | 0 to +100GWh |  | Y, R, U
EnergyPosSumInt | Int32 | 0.1 Kilowatt Hours | 39 | Integer_Value (1000) | Energy, total positive (kWh) | 0 to +100GWh |  | Y, R, U
EnergyNegSum | Float | Kilowatt Hours | 40 | Present_Value (85) | Energy, total negative (kWh) | 0 to +100GWh |  | Y, R, U
EnergyNegSumInt | Int32 | 0.1 Kilowatt Hours | 40 | Integer_Value (1000) | Energy, total negative (kWh) | 0 to +100GWh |  | Y, R, U
EnergyA | Float | Kilowatt Hours | 41 | Present_Value (85) | Energy, phase A | ±100GWh |  | Y, R, U
EnergyAInt | Int32 | 0.1 Kilowatt Hours | 41 | Integer_Value (1000) | Energy, phase A | ±100GWh |  | Y, R, U
EnergyB | Float | Kilowatt Hours | 42 | Present_Value (85) | Energy, phase B | ±100GWh |  | Y, R, U
EnergyBInt | Int32 | 0.1 Kilowatt Hours | 42 | Integer_Value (1000) | Energy, phase B | ±100GWh |  | Y, R, U
EnergyC | Float | Kilowatt Hours | 43 | Present_Value (85) | Energy, phase C | ±100GWh |  | Y, R, U
EnergyCInt | Int32 | 0.1 Kilowatt Hours | 43 | Integer_Value (1000) | Energy, phase C | ±100GWh |  | Y, R, U
EnergyPosA | Float | Kilowatt Hours | 44 | Present_Value (85) | Energy, positive, phase A | 0 to +100GWh |  | Y, R, U
EnergyPosAInt | Int32 | 0.1 Kilowatt Hours | 44 | Integer_Value (1000) | Energy, positive, phase A | 0 to +100GWh |  | Y, R, U
EnergyPosB | Float | Kilowatt Hours | 45 | Present_Value (85) | Energy, positive, phase B | 0 to +100GWh |  | Y, R, U
EnergyPosBInt | Int32 | 0.1 Kilowatt Hours | 45 | Integer_Value (1000) | Energy, positive, phase B | 0 to +100GWh |  | Y, R, U
EnergyPosC | Float | Kilowatt Hours | 46 | Present_Value (85) | Energy, positive, phase C | 0 to +100GWh |  | Y, R, U
EnergyPosCInt | Int32 | 0.1 Kilowatt Hours | 46 | Integer_Value (1000) | Energy, positive, phase C | 0 to +100GWh |  | Y, R, U
EnergyNegA | Float | Kilowatt Hours | 47 | Present_Value (85) | Energy, negative, phase A | 0 to +100GWh |  | Y, R, U
EnergyNegAInt | Int32 | 0.1 Kilowatt Hours | 47 | Integer_Value (1000) | Energy, negative, phase A | 0 to +100GWh |  | Y, R, U
EnergyNegB | Float | Kilowatt Hours | 48 | Present_Value (85) | Energy, negative, phase B | 0 to +100GWh |  | Y, R, U
EnergyNegBInt | Int32 | 0.1 Kilowatt Hours | 48 | Integer_Value (1000) | Energy, negative, phase B | 0 to +100GWh |  | Y, R, U
EnergyNegC | Float | Kilowatt Hours | 49 | Present_Value (85) | Energy, negative, phase C | 0 to +100GWh |  | Y, R, U
EnergyNegCInt | Int32 | 0.1 Kilowatt Hours | 49 | Integer_Value (1000) | Energy, negative, phase C | 0 to +100GWh |  | Y, R, U
EnergyReacSum | Float | kVARh | 50 | Present_Value (85) | Reactive energy, total | ±100GWh |  | Y, R, U
EnergyReacSumInt | Int32 | 0.1 kVARh | 50 | Integer_Value (1000) | Reactive energy, total | ±100GWh |  | Y, R, U
EnergyReacA | Float | kVARh | 51 | Present_Value (85) | Reactive energy, phase A | ±100GWh |  | Y, R, U
EnergyReacAInt | Int32 | 0.1 kVARh | 51 | Integer_Value (1000) | Reactive energy, phase A | ±100GWh |  | Y, R, U
EnergyReacB | Float | kVARh | 52 | Present_Value (85) | Reactive energy, phase B | ±100GWh |  | Y, R, U
EnergyReacBInt | Int32 | 0.1 kVARh | 52 | Integer_Value (1000) | Reactive energy, phase B | ±100GWh |  | Y, R, U
EnergyReacC | Float | kVARh | 53 | Present_Value (85) | Reactive energy, phase C | ±100GWh |  | Y, R, U
EnergyReacCInt | Int32 | 0.1 kVARh | 53 | Integer_Value (1000) | Reactive energy, phase C | ±100GWh |  | Y, R, U
EnergyAppSum | Float | kVAh | 54 | Present_Value (85) | Apparent energy, total | 0 to +100GWh |  | Y, R, U
EnergyAppSumInt | Int32 | 0.1 kVAh | 54 | Integer_Value (1000) | Apparent energy, total | 0 to +100GWh |  | Y, R, U
EnergyAppA | Float | kVAh | 55 | Present_Value (85) | Apparent energy, phase A | 0 to +100GWh |  | Y, R, U
EnergyAppAInt | Int32 | 0.1 kVAh | 55 | Integer_Value (1000) | Apparent energy, phase A | 0 to +100GWh |  | Y, R, U
EnergyAppB | Float | kVAh | 56 | Present_Value (85) | Apparent energy, phase B | 0 to +100GWh |  | Y, R, U
EnergyAppBInt | Int32 | 0.1 kVAh | 56 | Integer_Value (1000) | Apparent energy, phase B | 0 to +100GWh |  | Y, R, U
EnergyAppC | Float | kVAh | 57 | Present_Value (85) | Apparent energy, phase C | 0 to +100GWh |  | Y, R, U
EnergyAppCInt | Int32 | 0.1 kVAh | 57 | Integer_Value (1000) | Apparent energy, phase C | 0 to +100GWh |  | Y, R, U
ThermistorTemp | Float | C | 58 | Present_Value (85) | Thermistor temperature | none |  | N
Analog Value Objects (Object_Type = 2)
ErrorStatus1 | Float | No Units | 0 | Present_Value (85) | Most recent error code | none | 0 | R, U
ErrorStatus1Time | UInt32 | Seconds | 0 | Time_Value (2000) | Error code time stamp (TotalSecs) | none | 0 | R, U
ErrorStatus2 | Float | No Units | 1 | Present_Value (85) | 2nd most recent error code | none | 0 | R, U
ErrorStatus2Time | UInt32 | Seconds | 1 | Time_Value (2000) | Error code time stamp (TotalSecs) | none | 0 | R, U
ErrorStatus3 | Float | No Units | 2 | Present_Value (85) | 3rd most recent error code | none | 0 | R, U
ErrorStatus3Time | UInt32 | Seconds | 2 | Time_Value (2000) | Error code time stamp (TotalSecs) | none | 0 | R, U
ErrorStatus4 | Float | No Units | 3 | Present_Value (85) | 4th most recent error code | none | 0 | R, U
ErrorStatus4Time | UInt32 | Seconds | 3 | Time_Value (2000) | Error code time stamp (TotalSecs) | none | 0 | R, U
ErrorStatus5 | Float | No Units | 4 | Present_Value (85) | 5th most recent error code | none | 0 | R, U
ErrorStatus5Time | UInt32 | Seconds | 4 | Time_Value (2000) | Error code time stamp (TotalSecs) | none | 0 | R, U
ErrorStatus6 | Float | No Units | 5 | Present_Value (85) | 6th most recent error code | none | 0 | R, U
ErrorStatus6Time | UInt32 | Seconds | 5 | Time_Value (2000) | Error code time stamp (TotalSecs) | none | 0 | R, U
ErrorStatus7 | Float | No Units | 6 | Present_Value (85) | 7th most recent error code | none | 0 | R, U
ErrorStatus7Time | UInt32 | Seconds | 6 | Time_Value (2000) | Error code time stamp (TotalSecs) | none | 0 | R, U
ErrorStatus8 | Float | No Units | 7 | Present_Value (85) | 8th most recent error code | none | 0 | R, U
ErrorStatus8Time | UInt32 | Seconds | 7 | Time_Value (2000) | Error code time stamp | none | 0 | R, U
UptimeSecs | Float | Seconds | 8 | Present_Value (85) | Runtime since last power cycle | none | 0 | N
TotalSecs | Float | Seconds | 9 | Present_Value (85) | Total accumulated runtime | none | 0 | N
PowerFailCount | Float | No Units | 10 | Present_Value (85) | Total accumulated power cycles | none | 1 | N
ConfigPasscode | Float | No Units | 11 | Present_Value (85) | Unlock user protected access, 0-unlocked, 1-locked | any | 0 | Y
CtAmpsA | Float | Amperes | 12 | Present_Value (85) | CT amps, phase A | 0 to 60000 | 5 | Y, U
CtAmpsB | Float | Amperes | 13 | Present_Value (85) | CT amps, phase B | 0 to 60000 | 5 | Y, U
CtAmpsC | Float | Amperes | 14 | Present_Value (85) | CT Amps, phase C | 0 to 60000 | 5 | Y, U
DemPerMins | Float | Minutes | 15 | Present_Value (85) | Demand period, minutes | 1 to 720 | 15 | Y, U
DemSubints | Float | No Units | 16 | Present_Value (85) | Demand subinterval count | 1 to 10 | 1 | Y, U
GainAdjustA | Float | No Units | 17 | Present_Value (85) | Power/energy gain adjust, phase A | 5000 to 20000 | 10000 | Y, U
GainAdjustB | Float | No Units | 18 | Present_Value (85) | Power/energy gain adjust, phase B | 5000 to 20000 | 10000 | Y, U
GainAdjustC | Float | No Units | 19 | Present_Value (85) | Power/energy gain adjust, phase C | 5000 to 20000 | 10000 | Y, U
PhaseAdjustA | Float | Degrees Angular | 20 | Present_Value (85) | CT phase angle adjust, phase A | -8000 to +8000 | -1000 | Y, U
PhaseAdjustB | Float | Degrees Angular | 21 | Present_Value (85) | CT phase angle adjust, phase B | -8000 to +8000 | -1000 | Y, U
PhaseAdjustC | Float | Degrees Angular | 22 | Present_Value (85) | CT phase angle adjust, phase C | -8000 to +8000 | -1000 | Y, U
CreepLimit | Float | No Units | 23 | Present_Value (85) | Minimum power for non-zero readings | 100 to 10000 | 1500 | Y, U
PtRatio | Float | No Units | 24 | Present_Value (85) | Potential (voltage) transformer ratio | 0.05 to 300.0 | 1 | Y, U
Calibrate | Float | No Units | 25 | Present_Value (85) | Factory calibration object | any | 0 | Y
ThermistorCoeffA | Float | No Units | 35 | Present_Value (85) | Steinhart and Hart coefficient A | any | 0.0011274 | Y, U
ThermistorCoeffB | Float | No Units | 36 | Present_Value (85) | Steinhart and Hart coefficient B | any | 0.0002344 | Y, U
ThermistorCoeffC | Float | No Units | 37 | Present_Value (85) | Steinhart and Hart coefficient C | any | 8.6748e-08 | Y, U
Communication Error Count Objects (Object_Type = 2)
Rs485CollisionCount | Float | No Units | 26 | Present_Value (85) | RS-485 collision count | none | 0 | R, U
Rs485FramingErrorCount | Float | No Units | 27 | Present_Value (85) | RS-485 framing error count | none | 0 | R, U
FrameSizeErrorCount | Float | No Units | 28 | Present_Value (85) | Invalid frame data length count | none | 0 | R, U
HeaderCRCErrorCount | Float | No Units | 29 | Present_Value (85) | Header CRC errors | none | 0 | R, U
DataCRCErrorCount | Float | No Units | 30 | Present_Value (85) | Data CRC errors | none | 0 | R, U
IncompleteFrameCount | Float | No Units | 31 | Present_Value (85) | Received frame missing bytes | none | 0 | R, U
Rs485BreakCount | Float | No Units | 32 | Present_Value (85) | RS-485 break condition detected | none | 0 | R, U
BadByteCount | Float | No Units | 33 | Present_Value (85) | Received six unexpected bytes | none | 0 | R, U
LostToken | Float | No Units | 34 | Present_Value (85) | Timeout, token not received | none | 0 | R, U
Binary Value Objects (Object_Type = 5)
InvertCtA | Boolean | No Units | 0 | Present_Value (85) | Invert CT polarity, phase A | ACTIVE, INACTIVE | INACTIVE | Y, U
InvertCtB | Boolean | No Units | 1 | Present_Value (85) | Invert CT polarity, phase B | ACTIVE, INACTIVE | INACTIVE | Y, U
InvertCtC | Boolean | No Units | 2 | Present_Value (85) | Invert CT polarity, phase C | ACTIVE, INACTIVE | INACTIVE | Y, U
ClearErrors | Boolean | No Units | 3 | Present_Value (85) | Clear errors | ACTIVE, INACTIVE | INACTIVE | Y, U
ZeroEnergy | Boolean | No Units | 4 | Present_Value (85) | Resets energy registers | ACTIVE, INACTIVE | INACTIVE | Y, U
Wink | Boolean | No Units | 5 | Present_Value (85) | Display the LED wink pattern | ACTIVE, INACTIVE | INACTIVE | Y
Multi-State Value Objects (Object_Type = 19)
PhaseOffset | Enumerated | No Units | 0 | Present_Value (85) | Service type for line-to-line voltage estimates | 1 = Single-Phase 2 = 3-Ph Grounded Delta 3 = 3-Ph High-Leg Delta 4 = 3-Ph Balanced 5 = 1-Ph Center Neutral | 4 = Three Phase Balanced | Y, U
Averaging | Enumerated | No Units | 1 | Present_Value (85) | Measurement averaging | 1 = Fastest (1 sec.) 2 = Fast (5 sec.) 3 = Medium (20 sec.) 4 = Slow (60 sec.) | 2 = Fast | Y, U
ZeroDemand | Unsigned | No Units | 2 | Present_Value (85) | Reset demand or demand peaks | 1 = No Change 2 = Reset Min Max 3 =Start New Inteval 4 = Reset and Start | 1 = No Change | Y, U
Firmware Image File Object (Object_Type = 10)
File | BACnetObjectIdentifier |  | 0 | Object_Identifier (75) | Object identifier of the FirmwareImage object | none | 10 or 0 | N
File | String |  | 0 | Object_Name (77) | Name of the FirmewareImage object | none | FirmwareImage | N
File | BACnetObjectType |  | 0 | Object_Type (79) | 10 = file object type | none | 10 | N
File | String |  | 0 | Description (28) | WattNode BACnet firmware upgrade | none | WattNode BACnet firmware upgrade | N
File | String |  | 0 | File_Type (43) | Identifies the file type | none | Binary | N
File | Unsigned | Octets | 0 | File_Size (42) | Size of the file data in octets (bytes) | 32768 to 131072 | 0 | Y
File | BacnetDateTime |  | 0 | Modification_Date (71) | Always reports 2000-01-01 | none | 2000-01-01 12:00:00 | N
File | Boolean |  | 0 | Archive (13) | Has this file been modified since creation? Not used, reports TRUE or last value written. | TRUE (1), FALSE (0) | TRUE | Y
File | Boolean |  | 0 | Read_Only (99) | Is this file read-only? | none | FALSE | N
File | BacnetFileAccessMethod |  | 0 | File_Access_Method (41) | Type of file access supported | none | STREAM_ACCESS | N
Note on I1: Indicates if this register can be written: N = No Y = Yes R = May be reset to zero U = User passcode protectable
Note on I145: Although this object is writable, it is not possible to change the calibration without a unique passcode.